CONFIRMATION OF VERIFICATION EVIDENCE REPORT (COVER)

Medium Voltage Distributed Generation

(Instructions included on last page)

| ##### Section 1 | ##### FACILITIES INFORMATION |  |  |
| --- | --- | --- | --- |
| ###### Name of PROJECT |  |  |  |
| ###### name of CUSTOMER |  |  |  |
| ###### Proposed Energization Date |  |  |  |
| ###### PROJECT DESIGNATION |  |  |  |
| FEEDER NUMBER |  |  |  |
| ###### TRANSFORMER STATION |  |  |  |
| ##### Section 2 | ##### CONTACT INFORMATION |  |  |
| CUSTOMER CONTACT |  |  | GBE CONTACT |
| Print Name: Title: Tel. Email: |  |  | Print Name: Steve Faulkner Title: Manager, Metering & DERs Tel. 519-751-3522 x5672 Email: generation@grandbridgeenergy.com |

| ##### Section 3A | ##### TELEMETRY TESTS BEFORE ENERGIZATION |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Legend: C = Confirm Results: P = Pass, F = Fail All Parts: N/A = Not Applicable Confirm the following SCADA telemetry quantities: NOTE: Refer to Project specific Points List |  | Legend | Results | Initials | Date mm/dd/yyyy | Note # |
| Communication Link Test |  | C |  |  |  |  |
| DNP Protocol Link Test |  | C |  |  |  |  |
| MW Flows and Directions |  | C |  |  |  |  |
| MVAR Flow and Directions |  | C |  |  |  |  |
| Phase to Phase or Phase to Neutral Voltages |  | C |  |  |  |  |
| Three Phase Currents |  | C |  |  |  |  |
| HV or LV (circle one*) Interrupter Open/Close Status * GBE will specify which status points to use |  | C |  |  |  |  |
| Protection Alarms (TT Receive, DGEO Send) |  | C |  |  |  |  |
| Other (Specify) |  | C |  |  |  |  |

| ##### Section 3B | ##### VERIFICATION-PROTECTION & CONTROL |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Legend: C = Confirm Results: P = Pass, F = Fail, N/A = Not Applicable |  | Legend | Results | Initials | Date mm/dd/yyyy | Note # |
| - Is commissioning in compliance with the submitted Commissioning plans? |  | C |  |  |  |  |
| - Are reviewed GrandBridge Energy (‘GBE’) approved relay settings applied? |  | N/A |  |  |  |  |
| Confirm that the following protection systems, as applicable, have been verified to function as per the design: NOTE: Tests marked with an asterisk (*) require coordination with GBE |  |  |  |  |  |  |
| - Feeder Protection per CSA and/or IEEE |  | C |  |  |  |  |
| - LV Breaker Failure Protection and Reclose |  | C |  |  |  |  |
| - Under and Over Frequency per CSA and/or IEEE |  | C |  |  |  |  |
| - Under and Over Voltage per CSA and/or IEEE |  | C |  |  |  |  |
| - Passive Anti-Islanding (for Inverter Based Generators) * |  | N/A |  |  |  |  |
| - Transfer Trip / Remote Trip * |  | C |  |  |  |  |
| - DGEO (Generator End Open) * |  | C |  |  |  |  |
| - Gen. Prot. That trips HV Sync breakers |  | C |  |  |  |  |
| - Instrument Transformer (eg. CTS + CCVTs, etc.) |  | C |  |  |  |  |
| - Monitoring Equipment (eg. DRR, SER, etc.) |  | C |  |  |  |  |
| - Other (For customer use to specify additional tests) |  | C |  |  |  |  |

| ##### Section 4 | ##### CONFIRMATION OF VERIFICATION-POWER EQUIPMENMT |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Legend: C = Confirm Result: P = Pass, F = Fail All Parts: N/A = Not Applicable |  | Legend | Result | Initial | Date mm/dd/yyyy | Note # |
| - Verify the HV/LV disconnect switches/circuit switchers are suitable as an isolation point per Utility Work Protection Code? NOTE: Any future modifications to the isolation device(s) used to provide supporting guarantees to GBE under the Utility Work Protection Code must be re-verified. |  | C |  |  |  |  |
| - Confirm correct operation of the HV/LV disconnect switches/circuit switchers/breakers |  | C |  |  |  |  |
| - Is closing time within manufacturer’s specification? |  | C |  |  |  |  |
| - Is opening time within manufacturer’s specification? |  | C |  |  |  |  |
| - Are the specified HV/LV surge arrestors installed? |  | C |  |  |  |  |
| - Confirm interface transformers connected correctly as per the design. |  | C |  |  |  |  |
| - Confirm the DC system installed (ie battery, charger, dc panel, dc monitoring)? |  | C |  |  |  |  |
| - Does the LV equipment (ie, disconnect switches, circuit switchers, breakers, CVTs, CTs) have the appropriate voltage class and current ratings as per the submitted Single Line Diagram? |  | C |  |  |  |  |
| - Other (specify) - DZTT |  | C |  |  |  |  |

| ##### Section 5 | ##### ELECTRICAL SAFETY |  |  |
| --- | --- | --- | --- |
| Legend: SD = Supporting Document, N/A = Not Applicable |  | Legend | Date mm/dd/yyyy |
| - Prior to energizing any new or modified customer or generator facilities, Electrical Safety Authority (ESA) must provide a Temporary Connection Authorization (Ontario Electrical Safety Code Article 2-014). Attach document. |  | SD |  |
| - Prior to final in-service of new or modified customer or generator facilities, ESA must provide Connection Authorization (Code Article 2-012). Attach document. |  | SD |  |
| - All customers must provide a letter signed and stamped by a Professional Engineer registered in the Province of Ontario stating that their equipment and installation meets CSA and/or other applicable electrical safety standards, prior to ready for Service Date. Attach document. |  | SD |  |

| The Generation Coordinator approves the proposed checks, verifications, tests and notes submitted by the customer for the scheduled COVER. | ## Generation Coordinator Initials |
| --- | --- |

NOTES:  (For use with Sections 3, 4 & 5)

| #: | Comments: | Generation Coordinator Concurrence to Connect: | Date Action Resolved: (dd/mm/yyyy) |
| --- | --- | --- | --- |

| ##### Section 6A | ##### SIGN OFF TO CONNECT AS A LOAD (IF APPLICABLE) (New Connection – Milestone #1) Please check Applicable Not Applicable |  |
| --- | --- | --- |
| By signing* this form, the customer acknowledges the following: - All required verifications in Sections 3, 4 and 5 specified under this COVER document have been completed. - The generator facility design and operation meets the minimum standards for generator facilities connected to a distribution system, as per the Distribution System Code. - The equipment and installation meet CSA and/or other applicable electrical safety standards. - The generator holds an OEB Electricity Generation License, if required. |  | Signature of Customer Representative (Note: Must be P. Eng licensed in Ontario) Print Name: Title: Date: Must affix P.Eng seal (stamp here): |
| *After signing the COVER, the customer shall submit it to the GBE Generation Coordinator. |  |  |

| GBE’s Generation Coordinator has reviewed the customer’s Certified COVER document and the customer’s facility may be connected to the grid as a load. | Signature of GBE Generation Coordinator Print Name: Title: Date: |
| --- | --- |
| GBE Generation Coordinator shall notify Customer Service and Operations to proceed with the connection |  |

| ##### Section 6B | ##### SIGN OFF TO CONNECT AS A LOAD ##### WITH GENERATOR TESTING RIGHTS (New Connection – Milestone #2 OR Existing Connection – Modification) Please check Applicable Not Applicable |  |
| --- | --- | --- |
| By signing* this form, the customer acknowledges the following: - All required verifications specified in Sections 3, 4 and 5 under this COVER document have been completed. - The generator facility design and operation meets the minimum standards for generator facilities connected to a distribution system, as per the Distribution System Code. - The equipment and installation meet CSA and/or other applicable electrical safety standards. - The generator holds an OEB Electricity Generation License, if required. |  | Signature of Customer Representative (Note: Must be P. Eng licensed in Ontario) Print Name: Title: Date: Must affix P.Eng seal (stamp here): |
| *After signing the COVER, the customer shall submit it to the GBE Generation Coordinator. |  |  |

| GBE’s Generation Coordinator has reviewed the customer’s Certified COVER document and the customer’s facility may be connected to the grid as a load with generator testing rights. | Signature of GBE Generation Coordinator Print Name: Title: Date: |
| --- | --- |
| GBE Generation Coordinator shall notify Customer Service and Operations to proceed with the connection |  |

| ##### Section 6C | ##### CONFIRM ON POTENTIAL/ON LOAD CHECKS AT RATED SYSTEM VOLTAGE (Milestone #3) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Legend: C = Confirm, Result: P = Pass, F = Fail All Parts: N/A = Not Applicable |  | Legend | Result | Initial | Date mm/dd/yyyy | Note # |
| Confirm phasor readings are completed and analyzed by the customer for protections listed in Section 3B. |  | C |  |  |  |  |
| Confirm online SCADA values (status/analog) per GBE approved SCADA Points List. |  | C |  |  |  |  |
| Live Test – verify grid-sense functionality (for inverters). Does the generator disconnect when the main service is disconnected? |  | N/A |  |  |  |  |
| Live Zone Test Trip (from Transfer Trip) / DGEO |  | C |  |  |  |  |

NOTES:  (For use with Section 6)

| #: | Comments: | Generation Coordinator Concurrence: | Date Action Resolved: (dd/mm/yyyy) |
| --- | --- | --- | --- |
| 1. |  |  |  |
| 2. |  |  |  |
| 3. |  |  |  |
| 4. |  |  |  |

I/we acknowledge the completion of the COVER as noted and the deficiencies identified in the “NOTES” section have been resolved.

Signature of Customer Representative (Note: Must be P. Eng,) Print Name: Title: Date:

GRANDBRIDGE ENERGY INC COVER ACCEPTANCE OF CONNECTION

________________________________________           ________________________________

Signature of Generation Coordinator                             Dated

| ##### Section 7 | ##### TEST SUMMARY REPORTS |
| --- | --- |

In accordance with the Distribution System Code, Appendix F, the Customer shall, at GBE request, provide GBE with a summary of testing results, including any certificates of inspection or other applicable authorizations or approvals certifying that any of the Customer's new, modified or replacement facilities have passed the relevant tests and comply with all applicable instruments and standards referred to in the code. This information will be kept on file for a period of (7) years by the Customer.

Distribution List (when all sections are completed): GBE Customer Agent HONI

Customer Instructions for Completing the COVER form

PART 1:  PLAN

Step 1:  Customer Information

    - Complete Facility and Customer Contact Information of the COVER Form by completing the highlighted portions of Sections 1 & 2. Proposed Energization Date should be a minimum of 2 weeks after commissioning.

Step 2:  Identify the Tests that the Customer Intends to Conduct

    - Complete Highlighted portions of Section 3A (Telemetry Tests Before Energization), where applicable.

    - Complete Highlighted portions (Protection Group and Legend columns) of Sections 3B, where applicable.

    - Complete Highlighted portions of Section 4 (Test Needed and Legend columns).

    - Complete Highlighted portions of Sections 5 (Legend column and Date Received column).

Note:  The design review must be finalized prior to completing this step.

Step 3:  GrandBridge Energy’s COVER Coordinator Review

    - Return COVER Form by email to the generation@grandbridgeenergy.com.

    - The COVER coordinator will review the proposed commission plan and respond to the acceptability of the proposed COVER tests within 5 business days.

Note:  The commissioning plan review must be finalized prior to commencing testing for the next step.

PART 2: PRE-ENERGIZATION

Step 4:  Completion of Testing and Resolution of all Comments

    - Complete all applicable testing in Sections 3A,3B,4, & 5.

    - Sign off the COVER, in section 6A or 6B, by a Customer P. Eng Representative, and submit it to the COVER Coordinator.

    - The COVER coordinator will review the certified COVER and recommend to GBE Operations Department for connection to the grid by signing section 6.

    - Section 6C testing can only proceed when all salient comments have been resolved and tests completed for Sections 3 to 6.

PART 3: POST-ENERGIZATION

Step 5:  Final Potential and On-load Checks

    - GBE will provide connection approval to the grid.

    - Complete and sign Section 6C when all parts of the COVER form are complete. (Note: cross readings to be performed within 5 business days of placing load on station)

    - Summary of testing results and certificates must be kept on file for a minimum period of 7 years by the Customer (as indicated by IESO Market Rules, Chp.4, 5.1.3).  GBE. may require this information, on an exception basis.

Step 6:  Record drawing submission

    - Submit record drawing (ie. As-built SLD) within 10 business days of energization.