## Common DER costs
GrandBridge Energy Common DER Connection Costs
No. | Cost Item* | Average Cost ($) |  |  |  |  | Note on potentially high variability factors affecting the cost item
|  | 0-12kW | 12-100kW | 101-500kW | 501kW-10MW | >10MW
1 | CIA Fee** | 0 | 2260 | 3640 | 8550 | * | GrandBridge Energy CIA fees. * No CIA requests >10MW to reference
2 | HOST CIA | 0 | 2054.41 | 3405.38 | 9011.83 | * | Hydro One CIA fees. *No fee posted for >10MW on HONI website
3 | SIA | N/A | N/A | N/A | N/A | * $20K | *Estimation. No reference costs within last 5 years
4 | Project Management | N/A | N/A | N/A | 5000 | $5-15K | Variable costs based on project scope
5 | Engineering | N/A | N/A | $0-5K | $5-10K | $5-10K | Variable costs based on project scope
6 | SCADA | N/A | N/A | N/A | $5-10K | $5-10K | Higher costs if Hydro One SCADA is also required
7 | Metering | 0 | 0 | 0 | 8000 | 8000 | Cost if Gross Load Billing metering for Hydro One is required
8 | LDC TX upgrade | N/A | $5-15K | $15-25K | $25-50K | * | Variable costs based on project scope * customer owned
9 | Transfer Trip | N/A | N/A | N/A | $250-400K | $250-400K | Cost vary based on communication medium (i.e.. Radio, fibre, etc.)
10 | Transfer Trip alternative | N/A | N/A | N/A | $50-100K | $50-100K | If alternative option is available based on project scope
*Associated labour costs are included in the charges
**Only fixed charge

## Cost variance template
GrandBridge Energy Guidance on Cost Variance template
DER Group/kW Size Range | No. | Project type (exporting/non-exporting) | Connection Cost Estimate ($) | Actual Connection Cost ($) | Variance [Actual - Estimate] ($) | Variance % | Expansion required (Y/N) | Transfer trip required (Y/N) | Build & Energization duration (Months) | General Notes
Group 1: Micro-DER (0-12kW) | 1 | Exporting | 509.58 | 509.58 | 0 | 0% | N | N | 4 to 6 | Single phase Net Metering fix fee for meter upgrade, labour, fleet
| 2 | Non-exporting | 0 | 0 | 0 | 0% | N | N | 4 to 6 | No fee for Micro-DER Non-exporting projects. Customer driven timeline
Group 2: Three Phase (13-500kW) | 1 | Exporting | 1150 | 1150 | 0 | 0% | N | N | 6 to 12 | No fee unless service upgrade required. Existing metering bi-directional
| 2 | Non-exporting | 0 | 0 | 0 | 0% | N | N | 6 to 12 | No fee unless service upgrade required. Existing metering bi-directional
Group 3: Three Phase (501-999kW) | 1 | Non-exporting | 22000 | 19913 | -2087 | -9.486% | N | N | 12 | Costs included typical admin., design review, and commissioning. SCADA required.
Group 4: Three Phase (>1mW) | 1 | Non-exporting | 737500 | 706723 | -30777 | -4.173% | Y | Y | 24 | Traditional transfer trip required (HONI station and GBE recloser). Costs included typical admin., design review, and commissioning. SCADA required.
| 2 | Non-exporting | 396200 | 366950 | -29250 | -7.383% | Y | Y | 18 | Alternate option to traditional transfer trip (Undervoltage supervision) implemented. Costs included typical admin., design review, and commissioning. SCADA required.
Notes: Groups 1 and 2 reflect costs in the past two years. Group 3 and 4 reflect costs in the past 5 years.